Earth leakage protection circuit :

# What is Leakage Current?

Suppose insulation fails.

Charger

Live ─────────► EV

               │
               │
             Person
               │
               ▼
             Earth

Neutral ◄────────

Now:

Live:

16 A

Neutral:

15.95 A

Difference:

16.00 A

-

15.95 A

=

0.05 A

Leakage:

50 mA

That missing current is flowing through the earth path instead of returning through neutral.

# Why is Leakage Dangerous?

Human body resistance varies:

- Dry skin → around 100 kΩ

- Wet skin → 1–5 kΩ

At 230 VAC:

Current can become dangerous very quickly.

Approximate physiological effects:

| Leakage Current | Effect |
| --- | --- |
| 1 mA | Barely perceptible |
| 5 mA | Mild shock |
| 10 mA | Painful shock |
| 30 mA | Muscle control may be lost |
| 50–100 mA | Potentially fatal |
| >100 mA | High risk of ventricular fibrillation |

This is why many protection devices trip around 30 mA.

# Differential Current Transformer (Core-Balance CT)

This is the most common sensing method in AC EV chargers.

## Construction

Ferrite Core

    ┌──────────────────┐

 Live ───────────────►

 Neutral ◄────────────

    └──────────────────┘

      Secondary Coil

           │

        Detection Circuit

Notice that both Live and Neutral pass through the same magnetic core.

# Normal Operation

Suppose:

Live:

20 A

Neutral:

20 A

Magnetic field from Live:

→

Magnetic field from Neutral:

←

They cancel.

Result:

Net Magnetic Flux = 0

Therefore:

No voltage is induced in the secondary winding.

The detector sees zero leakage.

# Leakage Condition

Suppose:

Live:

20 A

Neutral:

19.96 A

Difference:

40 mA

Now:

The magnetic fields no longer cancel completely.

Residual magnetic flux appears.

That changing residual flux induces a voltage in the secondary winding.

The detector measures this voltage.

More leakage → Larger induced signal.

# Normal Current Transformer (CT)

A normal CT measures the current in one conductor.

CT

      _________
     /         \
L ──►           ──► Load
     \_________/

Secondary → Meter / Relay

Only one conductor passes through the core.

If 20 A flows in the wire:

- Primary current = 20 A

- CT measures 20 A

Its purpose is current measurement and overcurrent protection.

# Core Balanced CT (CBCT)

A CBCT measures the difference between all conductors passing through the core.

CBCT

       ___________
      /           \
L ───►             ───►
N ───►             ───►
      \___________/

Secondary → Leakage detector

It does not measure the load current.

It measures only:

Residual Current

= Current leaving

− Current returning

# Can I pass both L and N through a normal CT?

This is where many people get confused.

Imagine taking a regular CT and passing both Live and Neutral through it.

CT

      _________
     /         \
L ──►           ───►
N ──►           ───►
     \_________/

Now think about what happens.

Normal operation:

L = 16 A

N = 16 A

The magnetic fields cancel.

The CT output becomes zero.

So, electromagnetically, it behaves like a CBCT.

# Then why are they different?

Because a normal CT is not designed or specified for residual current detection.

### 1. Core material

A load CT is optimized to measure large currents (e.g., 100 A, 500 A, 1000 A).

A CBCT is optimized to detect very small imbalances, such as:

- 30 mA

- 100 mA

- 300 mA

It uses a highly sensitive core with very low residual magnetism.

### 2. Sensitivity

Example:

A normal CT:

100 A primary

5 A secondary

It has poor sensitivity for tiny differences like 30 mA.

A CBCT is specifically designed so that a 30 mA residual current produces a detectable signal.

### 3. Accuracy

A normal CT is accurate over its rated current range.

A CBCT is accurate for residual current, even when the load current is hundreds of amperes.

Example:

Load current = 63 A

Leakage current = 30 mA

The CBCT must ignore the 63 A common-mode current and respond only to the 30 mA imbalance.

### 4. Electronics

A normal CT typically connects to:

- Ammeters

- Energy meters

- Overcurrent relays

A CBCT connects to:

- Earth leakage relay

- RCD/RCCB electronics

- Residual Current Monitor (RCM)

- EV charger controller

# A simple analogy

Think of two weighing devices.

### Normal CT

Like a weighing scale that measures:

Person weight

70 kg

It tells you the total weight.

### CBCT

Like a balance scale that compares two sides.

Left = 70 kg

Right = 69.97 kg

Difference = 30 g

It doesn't care about the total weight—it cares about the difference.

# Can a manufacturer make one CT work as a CBCT?

Yes, if it is designed for residual current sensing.

In fact, a CBCT is still a type of current transformer. The difference lies in its design and application.

So the relationship is:

Current Transformer (CT)
│
├── Measuring CT
│
├── Protection CT
│
└── Core Balanced CT (CBCT)

A CBCT is a specialized CT, but a standard measuring CT is not automatically suitable to be used as a CBCT.

### Practical takeaway for EV chargers

Inside an AC EV charger, you'll almost never see a standard current-measuring CT used for earth leakage detection. Instead, you'll find a dedicated CBCT or residual current sensor, because it must reliably detect leakage currents as low as 30 mA AC and, in many designs, 6 mA DC while ignoring tens of amperes of normal charging current. This high sensitivity is what distinguishes a CBCT from an ordinary CT.